## Summary
ASP House Portal report
Water & Wastewater Plant Review · exported Nov 4, 2026 5:16pm
Report | Rows
RO Plant | 6
Wastewater | 6
Required testing | 6
Water quality | 176

## RO Plant
Section | System / Area | Equipment / Tag | Observed Condition | Recommended Corrective Action | Responsible Party | Status | Latest Update | Update Date | Updated Since Review | Before Photos | After Photos
Pre-treatment | Multimedia filters | MMF-2 | Backwash valve slow to close; pressure drop across the filter above normal. | Rebuild the valve actuator and check the backwash timer. | Island Water | Complete | Actuator rebuilt and timer reset; pressure drop back to normal. | 2026-09-24 | Yes | 0 | 0
Pre-treatment | Cartridge filters | CF-1 | Cartridges changed later than the schedule. | Keep a change log at the housing and order a spare set. | Island Water | In Progress | Change log started; spare set on order. | 2026-09-25 | Yes | 0 | 0
RO trains | Train B | HPP-B | High-pressure pump seal weeping. | Replace the mechanical seal at the next planned shutdown. | Island Water | Open |  |  |  | 0 | 0
RO trains | Train A | RO-A | Normalized permeate flow down about 12% since spring. | Clean-in-place and send a membrane for autopsy if flow does not recover. | Island Water / TPU | In Progress | CIP done; flow up 8%. Watching for two more weeks. | 2026-09-27 | Yes | 0 | 0
Post-treatment | Chlorine dosing | CL-1 | Dosing pump has no spare on site. | Buy a spare pump and keep it in the store. | TPU | Complete | Spare pump delivered and shelved. | 2026-09-28 | Yes | 0 | 0
Storage | Tank B | TK-B | Hatch seal perished; small gap at the roof hatch. | Replace the hatch gasket and add a lock. | TPU | Open |  |  |  | 0 | 0

## Wastewater
Section | System / Area | Equipment / Tag | Observed Condition | Recommended Corrective Action | Responsible Party | Status | Latest Update | Update Date | Updated Since Review | Before Photos | After Photos
Headworks | Bar screen | BS-1 | Screenings bin overfilling at weekends. | Add a Saturday empty to the rota. | Island Water | Complete | Saturday empty added. | 2026-09-30 | Yes | 0 | 0
Aeration | Basin 2 | BL-2 | Blower 2 running hot; filter dirty. | Clean the intake filter and log blower temperatures weekly. | Island Water | Complete | Filter cleaned; temperatures logged weekly. | 2026-10-01 | Yes | 0 | 0
Aeration | Basin 1 | DO-1 | Dissolved oxygen probe reading low against the hand meter. | Calibrate the probe and replace the membrane cap. | Island Water | In Progress | Probe calibrated; new cap on order. | 2026-10-02 | Yes | 0 | 0
Clarifier | Clarifier 1 | CL-W1 | Scum baffle bracket corroded. | Replace the bracket with stainless. | TPU | Open |  |  |  | 0 | 0
Disinfection | UV channel | UV-1 | Two UV lamps past their rated hours. | Replace the lamps and record the hours. | Island Water | Noted | Lamps ordered with the quarterly parts. | 2026-10-04 | Yes | 0 | 0
Effluent | Irrigation pond | EP-1 | Fence gate does not latch. | Fix the latch and add a sign. | TPU | Complete | Latch fixed and sign up. | 2026-10-05 | Yes | 0 | 0

## Required testing
Plant | Test | Due | Countdown | Repeats | Last done | Note
Wastewater Plant | Sludge analysis | 2026-11-01 | 3 days overdue | Every 6 months | 2026-05-01
Wastewater Plant | Effluent BOD5 / TSS (outside lab) | 2026-11-06 | 2 days left | Every month | 2026-10-06
Drinking Water Plant (RO Plant) | Bacteriological sampling (distribution) | 2026-11-09 | 5 days left | Every week | 2026-11-02
Wastewater Plant | Nutrients (N and P) | 2026-11-23 | 19 days left | Every month | 2026-10-23
Drinking Water Plant (RO Plant) | Full chemical analysis (outside lab) | 2026-12-12 | 38 days left | Every 3 months | 2026-09-12
Drinking Water Plant (RO Plant) | Lead and copper (homes) | 2027-02-22 | 110 days left | Every year | 2026-02-22

## Water quality
Date | Plant | Lab | Sample point | Parameter | Result | Unit | Limit | Check | Notes
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 10 | mg/L | ≤ 30 | Within limit
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 9 | mg/L | ≤ 30 | Within limit
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.1 |  | 6.0 – 9.0 | Within limit
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 0.8 | mg/L
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 6.5 | mg/L
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 2.1 | mg/L
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 138 | per 100 mL
2026-11-02 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 2.10 | NTU
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.27 | mg/L | 0.2 – 4.0 | Within limit
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.09 | mg/L | ≤ 4.0 | Within limit
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.2 |  | 6.5 – 8.5 | Within limit
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.13 | NTU | ≤ 1.0 | Within limit
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 288 | mg/L | ≤ 500 | Within limit
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 402 | µS/cm
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-11-02 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 16 | mg/L | ≤ 30 | Within limit
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 14 | mg/L | ≤ 30 | Within limit
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.6 |  | 6.0 – 9.0 | Within limit
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 1.1 | mg/L
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 7.4 | mg/L
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 1.5 | mg/L
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 158 | per 100 mL
2026-10-26 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 2.15 | NTU
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 0.97 | mg/L | 0.2 – 4.0 | Within limit
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.68 | mg/L | ≤ 4.0 | Within limit
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.5 |  | 6.5 – 8.5 | Within limit
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.30 | NTU | ≤ 1.0 | Within limit
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 281 | mg/L | ≤ 500 | Within limit
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 540 | µS/cm
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-10-26 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 15 | mg/L | ≤ 30 | Within limit
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 13 | mg/L | ≤ 30 | Within limit
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.1 |  | 6.0 – 9.0 | Within limit
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 1.3 | mg/L
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 8.1 | mg/L
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 3.3 | mg/L
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 133 | per 100 mL
2026-10-19 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 2.73 | NTU
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.08 | mg/L | 0.2 – 4.0 | Within limit
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.47 | mg/L | ≤ 4.0 | Within limit
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.7 |  | 6.5 – 8.5 | Within limit
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.11 | NTU | ≤ 1.0 | Within limit
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 181 | mg/L | ≤ 500 | Within limit
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 446 | µS/cm
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-10-19 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 10 | mg/L | ≤ 30 | Within limit
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 12 | mg/L | ≤ 30 | Within limit
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.3 |  | 6.0 – 9.0 | Within limit
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 1.0 | mg/L
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 7.3 | mg/L
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 2.0 | mg/L
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 111 | per 100 mL
2026-10-12 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 2.48 | NTU
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.35 | mg/L | 0.2 – 4.0 | Within limit
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.76 | mg/L | ≤ 4.0 | Within limit
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.3 |  | 6.5 – 8.5 | Within limit
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.13 | NTU | ≤ 1.0 | Within limit
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 195 | mg/L | ≤ 500 | Within limit
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 542 | µS/cm
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-10-12 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 15 | mg/L | ≤ 30 | Within limit
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 6 | mg/L | ≤ 30 | Within limit
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.5 |  | 6.0 – 9.0 | Within limit
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 0.6 | mg/L
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 6.2 | mg/L
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 2.2 | mg/L
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 128 | per 100 mL
2026-10-05 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 1.79 | NTU
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.38 | mg/L | 0.2 – 4.0 | Within limit
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.53 | mg/L | ≤ 4.0 | Within limit
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.2 |  | 6.5 – 8.5 | Within limit
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.31 | NTU | ≤ 1.0 | Within limit
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 192 | mg/L | ≤ 500 | Within limit
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 506 | µS/cm
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-10-05 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 6 | mg/L | ≤ 30 | Within limit
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 16 | mg/L | ≤ 30 | Within limit
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.0 |  | 6.0 – 9.0 | Within limit
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 1.2 | mg/L
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 9.5 | mg/L
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 2.3 | mg/L
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 93 | per 100 mL
2026-09-28 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 2.18 | NTU
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.32 | mg/L | 0.2 – 4.0 | Within limit
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.84 | mg/L | ≤ 4.0 | Within limit
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.6 |  | 6.5 – 8.5 | Within limit
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.24 | NTU | ≤ 1.0 | Within limit
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 257 | mg/L | ≤ 500 | Within limit
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 446 | µS/cm
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-09-28 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 9 | mg/L | ≤ 30 | Within limit
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 10 | mg/L | ≤ 30 | Within limit
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.3 |  | 6.0 – 9.0 | Within limit
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 1.8 | mg/L
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 6.4 | mg/L
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 1.3 | mg/L
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 80 | per 100 mL
2026-09-21 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 6.80 | NTU
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.34 | mg/L | 0.2 – 4.0 | Within limit
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.34 | mg/L | ≤ 4.0 | Within limit
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.6 |  | 6.5 – 8.5 | Within limit
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.24 | NTU | ≤ 1.0 | Within limit
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 252 | mg/L | ≤ 500 | Within limit
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 477 | µS/cm
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-09-21 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 15 | mg/L | ≤ 30 | Within limit
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 9 | mg/L | ≤ 30 | Within limit
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.0 |  | 6.0 – 9.0 | Within limit
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 0.9 | mg/L
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 10.6 | mg/L
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 2.0 | mg/L
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 37 | per 100 mL
2026-09-14 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 1.62 | NTU
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.60 | mg/L | 0.2 – 4.0 | Within limit
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.28 | mg/L | ≤ 4.0 | Within limit
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.2 |  | 6.5 – 8.5 | Within limit
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.13 | NTU | ≤ 1.0 | Within limit
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 226 | mg/L | ≤ 500 | Within limit
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 536 | µS/cm
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-09-14 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 14 | mg/L | ≤ 30 | Within limit
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 15 | mg/L | ≤ 30 | Within limit
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.5 |  | 6.0 – 9.0 | Within limit
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 1.0 | mg/L
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 8.8 | mg/L
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 3.3 | mg/L
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 64 | per 100 mL
2026-09-07 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 3.25 | NTU
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.24 | mg/L | 0.2 – 4.0 | Within limit
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.38 | mg/L | ≤ 4.0 | Within limit
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.4 |  | 6.5 – 8.5 | Within limit
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.15 | NTU | ≤ 1.0 | Within limit
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 297 | mg/L | ≤ 500 | Within limit
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 368 | µS/cm
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-09-07 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 10 | mg/L | ≤ 30 | Within limit
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 14 | mg/L | ≤ 30 | Within limit
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.2 |  | 6.0 – 9.0 | Within limit
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 0.7 | mg/L
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 11.7 | mg/L
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 2.4 | mg/L
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 100 | per 100 mL
2026-08-31 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 3.42 | NTU
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.26 | mg/L | 0.2 – 4.0 | Within limit
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.76 | mg/L | ≤ 4.0 | Within limit
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.5 |  | 6.5 – 8.5 | Within limit
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.37 | NTU | ≤ 1.0 | Within limit
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 226 | mg/L | ≤ 500 | Within limit
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 411 | µS/cm
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-08-31 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | BOD5 | 8 | mg/L | ≤ 30 | Within limit
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | TSS | 15 | mg/L | ≤ 30 | Within limit
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | pH | 7.3 |  | 6.0 – 9.0 | Within limit
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | Ammonia (NH3-N) | 1.2 | mg/L
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | Total nitrogen | 10.5 | mg/L
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | Total phosphorus | 1.3 | mg/L
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | Fecal coliform | 49 | per 100 mL
2026-08-24 | Wastewater Plant | Island Water lab | Effluent to pond | Turbidity | 2.33 | NTU
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Free chlorine | 1.39 | mg/L | 0.2 – 4.0 | Within limit
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total chlorine | 1.98 | mg/L | ≤ 4.0 | Within limit
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | pH | 7.4 |  | 6.5 – 8.5 | Within limit
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Turbidity | 0.22 | NTU | ≤ 1.0 | Within limit
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | TDS | 299 | mg/L | ≤ 500 | Within limit
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Conductivity | 538 | µS/cm
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | Total coliform | Absent | per 100 mL | Absent | Within limit
2026-08-24 | Drinking Water Plant (RO Plant) | Island Water lab | Tank outlet | E. coli | Absent | per 100 mL | Absent | Within limit